## Heating Values
Heating Value and Relative Density Calculator |  |  |  |  | 0.11343 | 0.0070815 |  | 7.0669 | [8 empty] | 1.7519 |  |  |  |  | Water Saturation |  | Calculations based on IGT Bulletin No. 8. Water saturation calculated per "Steam Tables", Keenen, Keyes, Hill, and Moore
Calculations done per GPA 2172-09 w/ GPA 2145 Factors |  |  |  |  | TRUE | [7 empty] | DRY |  |  |  | WET |  |  |  | Norm. Factor
Instructions: Choose from the drop down which standard measurement of water vapor content was used then enter the measured value in the box below. Enter in the unnormalized mol% section the numbers from the unnormalized section of the gas analysis, or use the numbers from the normalized section if unnormalized is unavailable. | [20 empty] | 0.99072 |  | Input Data |  |  |  |  | Results |  |  | Tcritical | Pcritical | MWwater | Zwater | Std. Press | Std. Temp | R | deg R
[5 empty] | Ideal | Molar | b |  | Total | Total | Total |  |  | Total | Total | Total |  | Total | Total | Total | [10 empty] | 705.445 | 3203.6 | 18.0153 | 0.9996 | 14.73 | 60 | 10.731 | 459.67
[5 empty] | HV | mass |  |  | HV | mass | b |  | Normalized mol% | HV | mass | b | Normalized mol% | HV | mass | b | [5 empty] | Actual | Actual | Saturation | Saturation
|  |  | If Using Dewpoint, Enter Flowing Temp & Pressure Below |  | GPA 2145 Values | [11 empty] | 834 | [5 empty] | Flowing | Flowing | Water | Water | Water | Water | Water | Saturation | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 |  |  |  |  | water | water | IGT 8 | IGT 8 | [12 empty] | water | water | IGT 8 | IGT 8
54 |  |  | Flowing Temperature (deg F): | 0 | 1010 | 16.0425 | 0.0116 |  | 678.1564 | 10.7716 | 0.0077887 |  | 67.2204 | 678.9265 | 10.7838 | 0.0077976 | 66.0428 | 667.0322 | 10.5949 | 0.007661 |  | Meter ID | Pressure | Temp. | Dewpoint | Content | Content | Content | Content | Level | -741.9242 | -29.721 | -11.5529 | -0.86856 | 0.10941 | 0.43999 | 0.25207 | 0.052187 | Sum | Tau | K | Psat | fraction | content | correction | correction | [8 empty] | Sum | Tau | K | Psat | fraction | content | correction | correction
Component | Unnormalized mol% | Normalized mol% | Flowing Pressure (PSIA): | 0 | 1769.7 | 30.069 | 0.0238 |  | 308.5949 | 5.2433 | 0.0041502 |  | 17.4575 | 308.9454 | 5.2493 | 0.0041549 | 17.1517 | 303.5329 | 5.1573 | 0.0040821 |  |  | (psia) | (deg F) | (deg F) | (lb/MMcf) | (mole%) | (lbs/MMcf) | (mole%) | (%) | [11 empty] | (psia) |  | (lbs/MMcf) | (lbs/MMcf) | (mole frac) | [11 empty] | (psia) |  | (lbs/MMcf) | (lbs/MMcf) | (mole frac)
Methane | 67.773 | 67.1442 |  |  | 2516.1 | 44.0956 | 0.0347 |  | 196.4042 | 3.4421 | 0.0027086 |  | 7.8148 | 196.6272 | 3.446 | 0.0027117 | 7.6779 | 193.1825 | 3.3856 | 0.0026642
Ethane | 17.601 | 17.4377 | Results |  | 3251.9 | 58.1222 | 0.0441 |  | 30.8642 | 0.55164 | 0.00041856 |  | 0.95019 | 30.8992 | 0.55227 | 0.00041903 | 0.93354 | 30.3579 | 0.5426 | 0.00041169 |  | Input | 0 | 0 | 54 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | -741.9242 | -15.6861 | -3.218 | -0.12769 | 0.0084891 | 0.018018 | 0.0054478 | 0.00059528 | -760.9235 | 3.5042 | -9.6502 | 0.20636 | #DIV/0! | #DIV/0! | 4.9198 | 0.00010335 | -741.9242 | -24.6024 | -7.9162 | -0.49265 | 0.05137 | 0.17101 | 0.081095 | 0.013898 | -774.6181 | 3.9159 | -11.8879 | 0.022019 | #DIV/0! | #DIV/0! | 0.9722 | 2.0422e-05
Propane | 7.879 | 7.8059 | True Real Heating Value: | 1368.6442 | 3262.3 | 58.1222 | 0.047 |  | 83.742 | 1.492 | 0.0012065 |  | 2.5699 | 83.8371 | 1.4937 | 0.0012078 | 2.5249 | 82.3683 | 1.4675 | 0.0011867
I-Butane | 0.958 | 0.94911 | True Relative Density: | 0.81393 | 4000.9 | 72.1488 | 0.0576 |  | 18.9865 | 0.34239 | 0.00027334 |  | 0.47509 | 19.0081 | 0.34278 | 0.00027365 | 0.46677 | 18.6751 | 0.33677 | 0.00026886
n-Butane | 2.591 | 2.567 | Dry Real Heating Value: | 1370.1601 | 4008.7 | 72.1488 | 0.0606 |  | 26.9665 | 0.48535 | 0.00040766 |  | 0.67346 | 26.9972 | 0.4859 | 0.00040812 | 0.66167 | 26.5242 | 0.47738 | 0.00040097
i-pentane | 0.479 | 0.47456 | Dry Relative Density: | 0.81413 | 4755.9 | 86.1754 | 0.0776 |  | 12.5333 | 0.2271 | 0.0002045 |  | 0.26383 | 12.5476 | 0.22736 | 0.00020473 | 0.25921 | 12.3277 | 0.22337 | 0.00020115
n-pentane | 0.679 | 0.6727 | Assumed Wet Real Heating Value: | 1346.7508 | 5129.22 | 93.1887 | 0.08637 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hexane | 0.266 | 0.26353 | Assumed Wet Relative Density: | 0.81116 | 5502.6 | 100.2019 | 0.0951 |  | 2.6167 | 0.047651 | 4.5224e-05 |  | 0.047609 | 2.6197 | 0.047705 | 4.5276e-05 | 0.046775 | 2.5738 | 0.046869 | 4.4483e-05
Hexane + | 0 | 0 | Ideal Heating Value: | 1359.3055 | 6249 | 114.2285 | 0.1128 |  | 0.37146 | 0.0067901 | 6.7052e-06 |  | 0.0059511 | 0.37188 | 0.0067978 | 6.7128e-06 | 0.0058468 | 0.36537 | 0.0066787 | 6.5952e-06
Heptane | 0.048 | 0.047555 | Ideal Gravity: | 0.81058 | 6996.3 | 128.2551 | 0.1307 |  | 0.069314 | 0.0012707 | 1.2949e-06 |  | 0.00099185 | 0.069393 | 0.0012721 | 1.2963e-06 | 0.00097447 | 0.068177 | 0.0012498 | 1.2736e-06
Octane | 0.006 | 0.0059443 | Zb (Compression factor) -gas | 0.99547 | 7742.9 | 142.2817 | 0.1556 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nonane | 0.001 | 0.00099072 | Zb (Compression Factor) -air | 0.99959 | 1599.7 | 28.0532 | 0.0207 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Decane | 0 | 0 | Unnormalized Sum Within 3% of 100%? 43 CFR 3175.118(b) | J | 2333 | 42.0797 | 0.0327 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ethylene | 0 | 0 |  |  | 0 | 44.0095 | 0.0195 |  | 0 | 0.38369 | 0.00017001 |  | 0.87283 | 0 | 0.38413 | 0.0001702 | 0.85753 | 0 | 0.3774 | 0.00016722
Propylene | 0 | 0 |  |  | 637.1 | 34.0809 | 0.0239 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CO2 | 0.88 | 0.87184 | API 14.5 Annex C Method |  | 0 | 28.0134 | 0.00442 |  | 0 | 0.4596 | 7.2516e-05 |  | 1.6425 | 0 | 0.46012 | 7.2598e-05 | 1.6137 | 0 | 0.45206 | 7.1327e-05
H2S | 0 | 0 |  |  | 0 | 31.9988 | 0.0072 |  | 0 | 0.0015851 | 3.5666e-07 |  | 0.0049592 | 0 | 0.0015869 | 3.5706e-07 | 0.0048724 | 0 | 0.0015591 | 3.5081e-07
Nitrogen | 1.656 | 1.6406 | This calculation is not the proper method |  | 0 | 4.0026 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Oxygen | 0.005 | 0.0049536 | Only use to check if the operator is using this method |  | 0 | 18.0153 | 0.0651 |  | 0 | 0.020435 | 7.3846e-05 |  |  | 0 | 0 | 0 | 1.7519 | 0 | 0.31561 | 0.0011405
Helium | 0 | 0 | Dry Heating Value from Gas Analysis: | 1370.2 | [7 empty] | 0.99185 |  |  |  |  | 0.97447
Water | 0.11343 | 0.11343 | True BTU Using Dry Value from BLM Calc: | 1368.6468 |  |  |  |  | 1359.3055 | 23.4765 | 0.017528 | 100.822 | 100 | 1360.8492 | 23.4827 | 0.017474 | 100 | 1337.0081 | 23.3869 | 0.018308
Sums | 100.822 | 100 | True BTU Using Dry Value from Operator: | 1368.6069
[15 empty] | 1360.8492 |  | Ideal Heating Value: |  |  |  | 1337.0081
[15 empty] | 0.8108 |  | Ideal Gravity: |  |  |  | 0.80749
[15 empty] | 0.9955 |  | Zb-gas |  |  |  | 0.99506
[15 empty] | 0.99959 |  | Zb-air |  |  |  | 0.99959
[15 empty] | 1370.1601 |  | Wet Real Heating Value: |  |  |  | 1346.7508
[15 empty] | 0.81413 |  | Wet Relative Density: |  |  |  | 0.81116
Water Vapor in lbs/MMscf
Water Vapor in mg/m3
Dewpoint (deg F)
1

## G.C. Fidelity Check
Only Use for Checking Gas Chromatograph Verification
G.C. Verification Fidelity Check
Linear Line on Graph Should Not Be Less Than ~0.99 - If so Likely Issue with Column, Verification Gas, or Detector
Molecule | Resp. Factor |  | Log Factor | Mol. Weight | Log Weight | Fidelity Graph
Methane | 4.195 | -4 | -3.3773 | 16.043 | 1.2053
Water |  | 1 | #N/A | 18.0153 | 1.2556
Carbon Mon. |  | 1 | #N/A | 28.01 | 1.4473
Nitrogen |  | 1 | #N/A | 28.0134 | 1.4474
Ethane | 2.83 | -4 | -3.5482 | 30.07 | 1.4781
H2S |  | 1 | #N/A | 34.08 | 1.5325
CO2 |  | 1 | #N/A | 44.01 | 1.6436
Propane | 2.221 | -4 | -3.6535 | 44.097 | 1.6444
Iso-butane |  | 1 | #N/A | 58.123 | 1.7643
n-butane | 1.852 | -4 | -3.7324 | 58.123 | 1.7643
iso-pentane |  | 1 | #N/A | 72.15 | 1.8582
n-pentane | 1.622 | -4 | -3.7899 | 72.15 | 1.8582
n-hexane |  | 1 | #N/A | 86.177 | 1.9354
n-heptane |  | 1 | #N/A | 100.204 | 2.0009
n-octane |  | 1 | #N/A | 114.231 | 2.0578
n-nonane |  | 1 | #N/A | 128.258 | 2.1081
n-decane |  | 1 | #N/A | 142.285 | 2.1532
〖10〗^𝑋

## Sheet2 (hidden)
Heating Value and Relative Density Calculation
Calculations done per GPA 2172-09
GPA 2145 Values
GPA 2145 |  | Ideal | Molar | b | Total | Total | Total
Component | mol% | HV | mass |  | HV | mass | b
Methane | 88.18 | 1010 | 16.0425 | 0.0116 | 890.618 | 14.1463 | 0.010229
Ethane | 4.31 | 1769.7 | 30.069 | 0.0238 | 76.2741 | 1.296 | 0.0010258
Propane | 0.86 | 2516.1 | 44.0956 | 0.0347 | 21.6385 | 0.37922 | 0.00029842
I-Butane | 0.22 | 3251.9 | 58.1222 | 0.0441 | 7.1542 | 0.12787 | 9.702e-05
n-Butane | 0.15 | 3262.3 | 58.1222 | 0.047 | 4.8935 | 0.087183 | 7.05e-05
i-pentane | 0.08 | 4000.9 | 72.1488 | 0.0576 | 3.2007 | 0.057719 | 4.608e-05
n-pentane | 0.09 | 4008.7 | 72.1488 | 0.0606 | 3.6078 | 0.064934 | 5.454e-05
Hexane | 0.13 | 4755.9 | 86.1754 | 0.0776 | 6.1827 | 0.11203 | 0.00010088
Hexane + | 0 | 5129.22 | 93.1887 | 0.08637 | 0 | 0 | 0
Heptane | 0.08 | 5502.6 | 100.2019 | 0.0951 | 4.4021 | 0.080162 | 7.608e-05
Octane | 0.04 | 6249 | 114.2285 | 0.1128 | 2.4996 | 0.045691 | 4.512e-05
Nonane | 0.01 | 6996.3 | 128.2551 | 0.1307 | 0.69963 | 0.012826 | 1.307e-05
Decane | 0 | 7742.9 | 142.2817 | 0.1556 | 0 | 0 | 0
Ethylene | 0 | 1599.7 | 28.0532 | 0.0207 | 0 | 0 | 0
Propylene | 0 | 2333 | 42.0797 | 0.0327 | 0 | 0 | 0
CO2 | 5.67 | 0 | 44.0095 | 0.0195 | 0 | 2.4953 | 0.0011056
H2S | 0 | 637.1 | 34.0809 | 0.0239 | 0 | 0 | 0
Nitrogen | 0.17 | 0 | 28.0134 | 0.00442 | 0 | 0.047623 | 7.514e-06
Oxygen | 0 | 0 | 31.9988 | 0.0072 | 0 | 0 | 0
Helium | 0 | 0 | 4.0026 | 0 | 0 | 0 | 0
Water | 0 | 50.31 | 18.0153 | 0.0651 | 0 | 0 | 0
Sums | 99.99 |  |  |  | 1021.1707 | 18.9528 | 0.01317
Ideal Heating Value: |  | 1021.1707
Ideal Gravity: |  | 0.65439
Zb-gas |  | 0.99745
Zb-air |  | 0.99959
Real Heating Value: |  | 1026.1548
Relative Density: |  | 0.6558

## Sheet3 (hidden)
Heating Value and Relative Density Calculation
Calculations done per GPA 2172-09
GPA 2145 Values
GPA 2145 |  | Ideal | Molar | b | Total | Total | Total
Component | mol% | HV | mass |  | HV | mass | b
Methane | 55.417 | 1010 | 16.0425 | 0.0116 | 559.7117 | 8.8903 | 0.0064284
Ethane | 18.908 | 1769.7 | 30.069 | 0.0238 | 334.6149 | 5.6854 | 0.0045001
Propane | 13.579 | 2516.1 | 44.0956 | 0.0347 | 341.6612 | 5.9877 | 0.0047119
I-Butane | 1.775 | 3251.9 | 58.1222 | 0.0441 | 57.7212 | 1.0317 | 0.00078277
n-Butane | 4.734 | 3262.3 | 58.1222 | 0.047 | 154.4373 | 2.7515 | 0.002225
i-pentane | 1.138 | 4000.9 | 72.1488 | 0.0576 | 45.5302 | 0.82105 | 0.00065549
n-pentane | 0.928 | 4008.7 | 72.1488 | 0.0606 | 37.2007 | 0.66954 | 0.00056237
Hexane | 0 | 4755.9 | 86.1754 | 0.0776 | 0 | 0 | 0
Hexane + | 0.576 | 5129.22 | 93.1887 | 0.08637 | 29.5443 | 0.53677 | 0.00049749
Heptane | 0 | 5502.6 | 100.2019 | 0.0951 | 0 | 0 | 0
Octane | 0 | 6249 | 114.2285 | 0.1128 | 0 | 0 | 0
Nonane | 0 | 6996.3 | 128.2551 | 0.1307 | 0 | 0 | 0
Decane | 0 | 7742.9 | 142.2817 | 0.1556 | 0 | 0 | 0
Ethylene | 0 | 1599.7 | 28.0532 | 0.0207 | 0 | 0 | 0
Propylene | 0 | 2333 | 42.0797 | 0.0327 | 0 | 0 | 0
CO2 | 1.031 | 0 | 44.0095 | 0.0195 | 0 | 0.45374 | 0.00020104
H2S | 0 | 637.1 | 34.0809 | 0.0239 | 0 | 0 | 0
Nitrogen | 1.913 | 0 | 28.0134 | 0.00442 | 0 | 0.5359 | 8.4555e-05
Oxygen | 0 | 0 | 31.9988 | 0.0072 | 0 | 0 | 0
Helium | 0 | 0 | 4.0026 | 0 | 0 | 0 | 0
Water | 0 | 50.31 | 18.0153 | 0.0651 | 0 | 0 | 0
Sums | 99.999 |  |  |  | 1560.4216 | 27.3636 | 0.020649
Ideal Heating Value: |  | 1560.4216
Ideal Gravity: |  | 0.9448
Zb-gas |  | 0.99372
Zb-air |  | 0.99959
Real Heating Value: |  | 1573.9169
Relative Density: |  | 0.95038

## normalize (hidden)
Heating Value and Relative Density Calculation
Calculations done per GPA 2172-09
GPA 2145 | Un-norm | Norm
Component | mol% | mol%
Methane | 89.2 | 86.9921
Ethane | 7.8 | 7.6069
Propane | 3 | 2.9257
I-Butane | 0 | 0
n-Butane | 0 | 0
i-pentane | 1 | 0.97525
n-pentane | 0 | 0
Hexane | 0 | 0
Hexane + | 0 | 0
Heptane | 0 | 0
Octane | 0 | 0
Nonane | 0 | 0
Decane | 0 | 0
Ethylene | 0 | 0
Propylene | 0 | 0
CO2 | 0 | 0
H2S | 0 | 0
Nitrogen | 0 | 0
Oxygen | 0 | 0
Helium | 0 | 0
Water | 1.5 | 1.4851 | <--not normalized
Sums (non H2O) | 101 | 99.9851
Total | 102.5

## Sheet4 (hidden)
0.5548 | 0.556 | -0.0012 | 0.1944
0.6 | 0.6006 | -0.0006 | 0.083229
0.6221 | 0.6223 | -0.0002 | 0.025829
0.7 | 0.6991 | 0.0009 | -0.091985
0.8 | 0.7976 | 0.0024 | -0.18821
0.9 | 0.8963 | 0.0037 | -0.22957